ENGINEERING SPECIFICATION

SYMCOM MODEL 355-200

3-PHASE VOLTAGE MONITOR/PROTECTION RELAY

- GENERAL

  - REFERENCES

    - UL 508 Industrial Control Equipment – Underwriters Laboratories

    - IEC 60947 Low Voltage Switchgear and Controlgear – International Electrotechnical Commission

    - ANSI/IEEE C62.41 – American National Standards Institute/Institute of Electrical & Electronics Engineers

  - WARRANTY

A.  Manufacturer Warranty:  The manufacturer shall guarantee the equipment to be free from material and workmanship defects for a period of five years from the date of manufacture when installed and operated according to the manufacturer’s requirements.

- PRODUCTS

  - MANUFACTURERS

The equipment specified shall be the Model 355-200, manufactured by SymCom, Inc.

  - DESCRIPTION

    - Regulatory Requirements:

      - The equipment shall be UL Listed as type NKCR—Industrial Control Equipment-Motor Controllers-Auxiliary Devices.

      - The equipment shall be ULC Listed as type NKCR7—Industrial Control Equipment-Motor Controllers-Auxiliary Devices Certified for Canada.

  - Performance/Design Criteria:  3-Phase Voltage Monitor/Protection Relay

    - Protective Relay Functions

      - The equipment shall provide protection against the following conditions:

        - phase loss

        - phase reversal

        - low voltage

        - voltage unbalance

        - rapid cycling due to power faults*

f.   high voltage

    - Capabilities and Features

      - Inputs

        - The equipment shall accept 3-phase input voltage range from 190-240VAC, adjustable.

        - The equipment shall accept 3-phase voltage at 50/60Hz.

      - Outputs

        - The equipment shall include one Form C (SPDT) output relay.  Contacts pilot duty rated 480VA@240VAC. Contacts general purpose rated 10A@240VAC.

      - The equipment shall include:

        - a low voltage trip of  90% of nominal setting

        - a high voltage trip of 110% of nominal setting

        - an adjustable phase unbalance trip point of 2-8%

        - an adjustable trip delay of 2-30 seconds for low voltage, high voltage, and unbalanced faults

        - a trip delay of 2 seconds for single-phasing faults (>25% voltage unbalance).

        - an adjustable restart delay of 2–300 seconds or manual restart

        - voltage accuracy  ±1%

      - The equipment shall include four indicator lights. The indicator lights have the capability to indicate whether the phase monitor is in run mode, restart delay mode, or fault mode.

        - Fault modes shall be low/high voltage, unbalance/single phase and phase reversal.

    - Electromagnetic Compatibility

      - The equipment shall be immune to electrostatic discharge per IEC 61000-4-2, Level 3, 6kV contact discharge and 8kV air discharge.

      - The equipment shall be immune to electrical fast transient bursts exceeding IEC 61000-4-4, Level 3.  Specified limits shall be 4kV.

      - The equipment shall be immune to electrical surges per IEC 61000-4-5.  Specified limits shall be Level 3, 4kV line-to-line, and Level 4, 4kV line-to-ground.

    - Dielectric Isolation:  Equipment withstands an alternating current potential of 1000V plus twice the rated voltage of the equipment for 1 minute without breakdown between uninsulated live parts and the enclosure with the contacts open and closed; between terminals of opposite polarity with the contacts closed; and between uninsulated live parts of different circuits.

*Using the adjustable restart delay to increase time before restart after a fault.

    - Environmental Requirements

      - The equipment shall operate continuously without derating in ambient temperatures of -40° to 70°C (-40° to 158°F).

      - The equipment shall operate continuously without derating in relative humidity of 10% up to 95% non-condensing per IEC 68-2-3.

      - The equipment shall operate properly after storage in ambient temperatures of -40° to 80°C (-40° to 176°F).

    - Dimensions:  The equipment dimensions shall not exceed 2.93” H X 5.27” W X 2.95” D.

    - Mounting:  The equipment shall be surface mountable.

End of Section