


             [image: image1.png]


          [image: image2.png]


         [image: image3.png]


                  


ENGINEERING SPECIFICATION

SYMCOM MODEL ACBC-120
ALARM CONTROLLER WITH BATTERY CHARGER
PART 1 GENERAL

1.1 REFERENCES
A. UL 508 Industrial Control Equipment – Underwriters Laboratories
B. IEC 60947 Low Voltage Switchgear and Controlgear – International Electrotechnical Commission
C. ANSI/IEEE C62.41 – American National Standards Institute/Institute of Electrical & Electronics Engineers 
D. CSA C22.2 No. 14 Industrial Control Equipment – Canadian Standards Association
1.2 WARRANTY
A. The manufacturer shall guarantee the equipment to be free from material and workmanship defects for a period of five years from the date of manufacture when installed and operated according to the manufacturer’s requirements.  
PART 2 PRODUCT
2.1 MANUFACTURERS

The equipment specified shall be the Model ACBC-120, manufactured by SymCom, Inc.
2.2 DESCRIPTION

A. Regulatory Requirements:
1. The equipment shall be UL Listed as type NKCR—Industrial Control Equipment-Motor Controllers-Auxiliary Devices.
2. The equipment shall be ULC Listed as type NKCR7—Industrial Control Equipment-Motor Controllers-Auxiliary Devices Certified for Canada.
3. The equipment shall be CE marked for use in the European Union and evaluated against IEC 60947 Low Voltage Switchgear and Controlgear.

2.3 Performance/Design Criteria: ALARM CONTROLLER WITH BACKUP BATTERY CHARGER
A. Capabilities and Features
1. Inputs

a. The equipment shall provide a horn silencing input.
b. The equipment shall accept single-phase input voltage rated 108-132VAC.

c. The equipment shall accept 12VDC from a lead-acid rechargeable battery.

2. Outputs

a. The equipment shall have the ability to charge a battery with the following currents:

1) 100mA +/- 10% in fast charge mode

2) 14mA +/- 50% in maintenance mode

b. The equipment shall have the ability to power a 12VDC, 1A external alarm strobe light from a battery.
c. The equipment shall have the ability to power a 12VDC, 1A external alarm horn from a battery for two seconds on and two seconds off.
3. Functional Specifications

a. The equipment shall have the following modes represented by two indicator LEDs:
1) Maintenance mode

2) Fast charge mode

3) Trip delay mode

4) Battery error mode

5) Low battery mode

6) Alarm mode

b. The equipment shall have a test button on the front of the unit.

c. The equipment shall be protected from the following battery conditions:
1) Battery connected in reverse polarity

2) Battery terminals short-circuited

d. The equipment shall have the ability to indicate the following battery conditions:

1) No battery present or battery connected in reverse polarity
2) Low battery voltage

B. Electromagnetic Compatibility
1. The equipment shall be immune to electrostatic discharge per IEC 61000-4-2, 6kV contact discharge and 8kV air discharge.
2. The equipment shall be immune to electrical fast transient bursts per IEC 61000-4-4.  Specified limits shall be Level 4 4kV.
3. The equipment shall be immune to electrical surges per IEC 61000-4-5.  Specified limits shall be Level 4 2kV line-to-line.
4. The equipment shall be immune to electrical surges per ANSI/IEEE C62.41 Surge and Ring Wave.  Specified limits shall be 6kV line-to-line.
5. The equipment shall be immune to radiated radio frequency emissions.  Specified limits shall be 10V/m at 150 MHz.
C. Dielectric Isolation:  Equipment withstands an alternating current potential of 1000V plus twice the rated voltage of the equipment for 1 minute without breakdown between uninsulated live parts and the enclosure with the contacts open and closed; between terminals of opposite polarity with the contacts closed; and between uninsulated live parts of different circuits.
D. Environmental Requirements
1. The equipment shall operate continuously without derating in surrounding air temperatures of -40° to 60°C (-40° to 140°F).
2. The equipment shall operate continuously without derating in relative humidity of 10% up to 95% non-condensing per IEC 68-2-3.
3. The equipment shall operate properly after storage in ambient temperatures of -40° to 80°C (-40° to 176°F).
E. Dimensions:  The equipment dimensions shall not exceed 1.750” high X 2.375” wide X 3.680” deep.
F. Mounting:
1. The equipment shall be mounted using the SymCom SD12-PC 12-pin rectangular socket.

a. The socket shall be 600V rated.

b. The socket shall be 10A rated.
c. The socket shall provide a means for mounting on the surface.
En SEQ CHAPTER \h \r 1d of Section
4-

ES-ACBC-120_A1 3/25/2010

[image: image1.png][image: image2.png][image: image3.png]